## Sheet1
SmartNode and HelioNode TrueCFM Backward Compatibility
CCU | CM | SN | Conclusion | Remarks
Updated | Not Updated | Not Updated | Loops would be operated on CCU
Updated | Updated | Not Updated | Loops would be operated on CCU |  |  |  | calculated damper pos
Updated | Updated | Updated | Loops would be operated on Edge after edge device is updated
< v2.17.x | <3.55 | <5.37 | NA
< v 2.17.x | < v3.55 | >= v5.37 | 1. CCU Sends RunPiLoopOnEdge field as '0' for VAV/ACB profiles. 2. New parameters on Edge are set to '0'. 3. To run the TrueCFM feature, both RunPiOnEdge and EnableCFM fields must be '1', which is not the case. 4. Therefore, Loop operation is handled by the CCU. |  | New Parameters - | 1. Settings2 Message a. MaxDAT 2. Controls Message a. CFM Airflow set point b. DAT set point 3. Regular Update a. Damper Position after CFM loop b. Reheat Damper Position after DAT loop
< v2.17.x | >= v3.55 | < v5.37 | 1. CCU sends RunPiLoopOnEdge field as '0' for VAV/ACB profiles. 2. CM reads both RunPiLoopOnEdge and new parameters as '0'. 3. SN ignores new fields. 4. Therefore, Loop doesn't run on Edge and is controlled by the CCU.
< v2.17.x | >= v3.55 | >= v5.37 | 1. CCU sends RunPiLoopOnEdge field as '0' for VAV/ACB profiles. 2. CM reads both RunPiLoopOnEdge and new parameters as '0'. 3. SN reads all new parameters as '0'. 4. Therefore, Loop doesn't run on Edge and is controlled by the CCU.
> = v2.17.x | < v3.55 | < v5.37 | 1. CCU sends RunPiLoopOnEdge field as '1' for VAV/ACB profiles and sends new parameters via Controls and Settings 2 message. 2. CM doesn’t receive new parameters of RU, SETTINGS2, and CONTROLS. 3. SN doesn’t understand RunPiLoopOnEdge field value '1' in VAV/ACB profiles. 4. Therefore, Loop doesn't run on Edge and will be controlled by the CCU. | Update CM and SN
> = v2.17.x | < v3.55 | >= v5.37 | 1. CCU sends RunPiLoopOnEdge field as '1' for VAV/ACB profiles and sends new parameters via Controls and Settings 2 message. 2. CM doesn’t receive new parameters of RU, SETTINGS2, and CONTROLS. 3. SN understands RunPiLoopOnEdge field value '1' in VAV/ACB profiles. 4. Therefore, Loop will run on Edge inproperly as Setpoints will not be sent by CM. | Update CM
> = v2.17.x | >= v3.55 | < v5.37 | 1. CCU sends RunPiLoopOnEdge field as '1' for VAV/ACB profiles and sends new parameters via Controls and Settings 2 message. 2. CM receives new parameters of RU, SETTINGS2, and CONTROLS. 3. SN doesn’t understand RunPiLoopOnEdge field value '1' in VAV/ACB profiles. 4. Therefore, Loop doesn't run on Edge and is controlled by the CCU. | Update SN
> = v2.17.x | >= v3.55 | >= v5.37 | TRUE CFM | Update All
CCU | CM | HN | Conclusion | Remarks
< v2.17.x | <3.55 | <6.29 | NA
< v 2.17.x | < v3.55 | >= v6.29 | 1. CCU Sends RunPiLoopOnEdge field as '0' for VAV/ACB profiles. 2. New parameters on Edge are set to '0'. 3. To run the TrueCFM feature, both RunPiOnEdge and EnableCFM fields must be '1', which is not the case. 4. Therefore, Loop operation is handled by the CCU.
< v2.17.x | >= v3.55 | < v6.29 | 1. CCU sends RunPiLoopOnEdge field as '0' for VAV/ACB profiles. 2. CM reads both RunPiLoopOnEdge and new parameters as '0'. 3. SN ignores new fields. 4. Therefore, Loop doesn't run on Edge and is controlled by the CCU.
< v2.17.x | >= v3.55 | >= v6.29 | 1. CCU sends RunPiLoopOnEdge field as '0' for VAV/ACB profiles. 2. CM reads both RunPiLoopOnEdge and new parameters as '0'. 3. SN reads all new parameters as '0'. 4. Therefore, Loop doesn't run on Edge and is controlled by the CCU.
> = v2.17.x | < v3.55 | < v6.29 | 1. CCU sends RunPiLoopOnEdge field as '1' for VAV/ACB profiles and sends new parameters via Controls and Settings 2 message. 2. CM doesn’t receive new parameters of RU, SETTINGS2, and CONTROLS. 3. SN doesn’t understand RunPiLoopOnEdge field value '1' in VAV/ACB profiles. 4. Therefore, Loop doesn't run on Edge and will be controlled by the CCU. | Update CM and SN
> = v2.17.x | < v3.55 | >= v6.29 | 1. CCU sends RunPiLoopOnEdge field as '1' for VAV/ACB profiles and sends new parameters via Controls and Settings 2 message. 2. CM doesn’t receive new parameters of RU, SETTINGS2, and CONTROLS. 3. SN understands RunPiLoopOnEdge field value '1' in VAV/ACB profiles. 4. Therefore, Loop will run on Edge inproperly as Setpoints will not be sent by CM. | Update CM
> = v2.17.x | >= v3.55 | < v6.29 | 1. CCU sends RunPiLoopOnEdge field as '1' for VAV/ACB profiles and sends new parameters via Controls and Settings 2 message. 2. CM receives new parameters of RU, SETTINGS2, and CONTROLS. 3. SN doesn’t understand RunPiLoopOnEdge field value '1' in VAV/ACB profiles. 4. Therefore, Loop doesn't run on Edge and is controlled by the CCU. | Update SN
> = v2.17.x | >= v3.55 | >= v6.29 | TRUE CFM | Update All