## Modbus Mapping
Register Type | Register Number | Register Type | Register Address | Parameters | Description | Type | Units | Values | BACnet Object ID
Holding Register | 40001 | Holding | 0 | Set Temperature Heating | Temperature setpoint hyperstat will heat to when operating mode = heating | uint16 | 2 x Fahrenheit | 120-180 (60.0 - 90.0) | 02
Holding Register | 40002 | Holding | 1 | Set Temperature Cooling | Temperature setpoint hyperstat will cool to when operating mode = cooling | uint16 | 2 x Fahrenheit | 120-180 (60.0 - 90.0) | 01
Holding Register | 40003 | Holding | 2 | Fan Speed | Configure the fan speed of hyperstat | uint8 | NA | 0 = OFF 1 = AUTO 2 = LOW 3 = MEDIUM 4 = HIGH | 03
Holding Register | 40004 | Holding | 3 | Conditioning Mode | Configure the conditioning mode of the hyperstat | uint8 | NA | 0 = OFF 1 = AUTO 2 = HEATING 3 = COOLING | 04
Holding Register | 40005 | Holding | 4 | Max Heating User Temp | Maximum heating set temperature user can set | uint16 | degrees Fahrenheit | 60-90 | 06
Holding Register | 40006 | Holding | 5 | Min Heating User Temp | Minimum heating set temperature the user can set | uint16 | degrees Fahrenheit | 60-90 | 07
Holding Register | 40007 | Holding | 6 | Max Cooling User Temp | Maximum cooling set temperature user can set | uint16 | degrees Fahrenheit | 60-90 | 08
Holding Register | 40008 | Holding | 7 | Min Cooling User Temp | Minimum cooling set temperature the user can set | uint16 | degrees Fahrenheit | 60-90 | 09
Holding Register | 40009 | Holding | 8 | Temperature Offset | Offset added to measurement room temperature | int16 | 1/10 degrees Fahrenheit | -100 - 100 (-10.0 - 10.0) | 10
Holding Register | 40010 | Holding | 9 | Heating Deadband | Amount above set temperature at which heating is activated | uint16 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0) | 11
Holding Register | 40011 | Holding | 10 | Cooling Deadband | Amount below set temperature at which cooling is activated | uint16 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0) | 12
Holding Register | 40012 | Holding | 11 | Temperature Mode | Temperature mode defining how temperature setpoints and deadbands can be configured and how they will be applied | uint8 | NA | 0 = Single Setpoint 1 = Dual Setpoint Fixed Deadband 2 = Dual Setpoint Variable Deadband | 13
Holding Register | 40013 | Holding | 12 | Humidity Min Setpoint | Threshold at which hyperstat will attempt to humidify if humidity level is less than | uint8 | % | 20-100 | 14
Holding Register | 40014 | Holding | 13 | Humidity Max Setpoint | Threshold at which hyperstat will attempt to dehumidify if humidity level is greater than | uint8 | % | 20-100 | 15
Holding Register | 40015 | Holding | 14 | CO2 Alert Threshold | Threshold of CO2 level at which an alert will be indicated | uint16 | ppm | 400-10000 | 16
Holding Register | 40016 | Holding | 15 | VOC Alert Threshold | Threshold of VOC level at which an alert will be indicated | uint16 | ppb | 0-10000 | 17
Holding Register | 40017 | Holding | 16 | PM2.5 Alert Threshold | Threshold of PM2.5 level at which an alert will be indicated | uint16 | ug/m3 | 0-10000 | 18
Holding Register | 40018 | Holding | 17 | Profile | Profile in which Hyperstat shall run | uint8 |  | 0 = None 1 = Conventional Package Unit 2 = Heat Pump Unit 3 = 2 Pipe Fancoil Unit 4 = 4 Pipe Fancoil Unit 5 = VRV 6 = Sense | 19
Holding Register | 40019 | Holding | 18 | Relay 1 Enable | Configure if relay 1 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 20
Holding Register | 40020 | Holding | 19 | Relay 2 Enable | Configure if relay 2 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 21
Holding Register | 40021 | Holding | 20 | Relay 3 Enable | Configure if relay 3 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 22
Holding Register | 40022 | Holding | 21 | Relay 4 Enable | Configure if relay 4 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 23
Holding Register | 40023 | Holding | 22 | Relay 5 Enable | Configure if relay 5 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 24
Holding Register | 40024 | Holding | 23 | Relay 6 Enable | Configure if relay 6 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 25
Holding Register | 40025 | Holding | 24 | Relay 1 Mapping | Configure the mapping of relay 1 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier | 26
Holding Register | 40026 | Holding | 25 | Relay 2 Mapping | Configure the mapping of relay 2 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier | 27
Holding Register | 40027 | Holding | 26 | Relay 3 Mapping | Configure the mapping of relay 3 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier | 28
Holding Register | 40028 | Holding | 27 | Relay 4 Mapping | Configure the mapping of relay 4 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier | 29
Holding Register | 40029 | Holding | 28 | Relay 5 Mapping | Configure the mapping of relay 5 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier | 30
Holding Register | 40030 | Holding | 29 | Relay 6 Mapping | Configure the mapping of relay 6 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier | 31
Holding Register | 40031 | Holding | 30 | Analog In 1 Enable | Configure if analog input 1 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 32
Holding Register | 40032 | Holding | 31 | Analog In 1 Mapping | Configure the mapping of analog input 1 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Current 0-10 1 = Current 0-20 2 = Current 0-50 3 = Keycard 4 = Door Window | 33
Holding Register | 40033 | Holding | 32 | Analog In 2 Enable | Configure if analog input 2 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 34
Holding Register | 40034 | Holding | 33 | Analog In 2 Mapping | Configure the mapping of analog input 2 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Current 0-10 1 = Current 0-20 2 = Current 0-50 3 = Keycard 4 = Door Window | 35
Holding Register | 40035 | Holding | 34 | Analog Out 1 Enable | Configure if analog output 1 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 36
Holding Register | 40036 | Holding | 35 | Analog Out 1 Mapping | Configure the mapping of analog output 1 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Cooling 1 = Fan Speed 2 = Heating 3 = DCV Damper | 37
Holding Register | 40037 | Holding | 36 | Analog Out 1 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 38
Holding Register | 40038 | Holding | 37 | Analog Out 1 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 39
Holding Register | 40039 | Holding | 38 | Analog Out 1 Pulse Enabled | Determines if PWM channel 1 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage | 40
Holding Register | 40040 | Holding | 39 | Analog Out 2 Enable | Configure if analog output 2 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 41
Holding Register | 40041 | Holding | 40 | Analog Out 2 Mapping | Configure the mapping of analog output 2 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Cooling 1 = Fan Speed 2 = Heating 3 = DCV Damper | 42
Holding Register | 40042 | Holding | 41 | Analog Out 2 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 43
Holding Register | 40043 | Holding | 42 | Analog Out 2 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 44
Holding Register | 40044 | Holding | 43 | Analog Out 2 Pulse Enabled | Determines if PWM channel 2 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage | 45
Holding Register | 40045 | Holding | 44 | Analog Out 3 Enable | Configure if analog output 3 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 46
Holding Register | 40046 | Holding | 45 | Analog Out 3 Mapping | Configure the mapping of analog output 3 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Cooling 1 = Fan Speed 2 = Heating 3 = DCV Damper | 47
Holding Register | 40047 | Holding | 46 | Analog Out 3 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 48
Holding Register | 40048 | Holding | 47 | Analog Out 3 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 49
Holding Register | 40049 | Holding | 48 | Analog Out 3 Pulse Enabled | Determines if PWM channel 3 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage | 50
Holding Register | 40050 | Holding | 49 | TH1 Airflow Temperature Enable | Enable or disable thermistor input 1 which is used for measuring airflow temperature | bool |  | 0 = Disabled 1 = Enabled | 51
Holding Register | 40051 | Holding | 50 | TH2 Enable | Enable or disable thermistor input 2 which is used for measuring airflow temperature | bool |  | 0 = Disabled 1 = Enabled | 52
Holding Register | 40052 | Holding | 51 | Use TH1 As Room Temp Sensor | When enabled, Hyperstat will use the thermistor connected at TH1 input for determining room/zone temperature instead of the onboard temperature sensor | bool |  | 0 = Disabled 1 = Enabled | 53
Holding Register | 40053 | Holding | 52 | Zone CO2 Damper Opening Rate | TBD | uint8 | %/100 ppm | 0-100 | 54
Holding Register | 40054 | Holding | 53 | Zone CO2 Threshold | Determines the point where Hyperstat starts controlling dampers to maintain CO2 at target value | uint16 | ppm | 0-2000 | 55
Holding Register | 40055 | Holding | 54 | Zone CO2 Target | Target value of CO2 | uint16 | ppm | 0-2000 | 56
Holding Register | 40056 | Holding | 55 | Proportional Constant | Tuner that produces an output action that is proportional to the deviation between the set point and the measured process value for a PI Loop | uint8 | 1/100 | 0-100 | 57
Holding Register | 40057 | Holding | 56 | Integral Constant | Condition with which the controller output is proportional to the amount of time the error is present | uint8 | 1/100 | 0-100 | 58
Holding Register | 40058 | Holding | 57 | Proportional Temperature Range | Defines the band of temperature, or range of temperature, over which the output of the controller is proportional. Example controlling the damper opertions | uint16 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0) | 59
Holding Register | 40059 | Holding | 58 | Integration Time | Defines the amount of time PI loop in the system integrates the error over a period until error value reaches to zero. It limits the speed of response and affects stability of the system | uint16 | minutes | 5-100 | 60
Holding Register | 40060 | Holding | 59 | Unoccupied Setback | Determines how many degrees from the desired temperature the zone will be allowed to drift during unoccupied | uint8 | 1/10 degrees Fahrenheit | 10-200 (1.0-20.0) | 61
Holding Register | 40061 | Holding | 60 | Relay Activation Hysteresis | Condition at which relay will turn off after being turned on to control based on load | uint8 | % | 1-50 | 62
Holding Register | 40062 | Holding | 61 | Analog Fan Speed Multiplier | Tuner that determines how fast a fan can move based on heating or cooling load | uint8 | 1/10 | 1-100 (0.1-10) | 63
Holding Register | 40063 | Holding | 62 | Humidity Hysteresis | Tuner that determines a condition at which humidier / dehumidifier will turn off after being turned on to control inside humidity | uint8 | % | 1-100 | 64
Holding Register | 40064 | Holding | 63 | Forced Occupied Time | During unoccupied time in case there is occupancy detected or user interacts with or edits user intent points then system enters in occupied mode for this tuner period only | uint8 | minutes | 0-255 | 65
Holding Register | 40065 | Holding | 64 | Auto Away Time | During Occupied period of the zone (Not during preconditioning period), If an Occupant is not detected for this tuner duration, the zone should enter 'Auto Away' mode if occupancy is enabled | uint8 | minutes | 0-255 | 66
Holding Register | 40066 | Holding | 65 | Auto Away Zone Setback Temp | Determines how many degrees from the desired temperature the zone will be allowed to drift during auto away | uint8 | 1/10 Degrees Fahrenheit | 10-200 (1.0 - 20.0) | 67
Holding Register | 40067 | Holding | 66 | FCU Aux Heating 1 Activate | Represents the difference between the current temp and heating desired temp in which the FCU Aux Heating 1 will activate. For example, if any relay is enabled and associated with Aux Heating State 1, the relay will be activated when currentTemp < Heating Desired Temp - FCU Aux Heating 1 Activate | uint8 | 1/10 Degrees Fahrenheit | 10-100 (1.0 - 10.0) | 68
Holding Register | 40068 | Holding | 67 | FCU Aux Heating 2 Activate | Represents the difference between the current temp and heating desired temp in which the FCU Aux Heating 2 will activate. For example, if any relay is enabled and associated with Aux Heating State 2, the relay will be activated when currentTemp < Heating Desired Temp - FCU Aux Heating 2 Activate | uint8 | 1/10 Degrees Fahrenheit | 10-100 (1.0 - 10.0) | 69
Holding Register | 40069 | Holding | 68 | FCU Two Pipe Heating Threshold | For a 2 pipe FCU, this tuner determines if the central plant is providing hot water when compared to supply water temp sensor. If Th2 (Supply water sensor) is more than 2pipeFancoilHeatingThreshold (85) then the central plant is providing hot water | uint8 | Degrees Fahrenheit | 70-130 | 70
Holding Register | 40070 | Holding | 69 | FCU Two Pipe Cooling Threshold | For a 2 pipe FCU, this tuner determines if the central plant is providing cold water when compared to supply water temp sensor. If Th2 (supply water sensor) is less than 2pipeFancoilCoolingThreshold (65) then the central plant is providing cold water | uint8 | Degrees Fahrenheit | 35-70 | 71
Holding Register | 40071 | Holding | 70 | FCU Water Valve Sampling On Time | If FCU water temperature is greater than FCU Two Pipe Heating Threshold Amount or less than FCU Two Pipe Cooling Threshold, then if the water valve relay has not been enabled for the last FCU Water Valve Sampling Wait Time, this value represents the amount of time the water valve relay will be enabled | uint8 | minutes | 0-30 | 72
Holding Register | 40072 | Holding | 71 | FCU Water Valve Sampling Wait Time | If FCU water temperature is greater than FCU Two Pipe Heating Threshold Amount or less than FCU Two Pipe Cooling Threshold, then if the water valve relay has been enabled for the last FCU Water Valve Sampling On Time, this value represents the amount of time the water valve relay will be disabled | uint8 | minutes | 5-255 | 73
Holding Register | 40073 | Holding | 72 | FCU Water Valve Sampling During Loop Deadband On Time | If FCU water temperature is between FCU Two Pipe Heating Threshold and FCU Two Pipe Cooling Threshold, then if the water valve relay has not been enabled for the last FCU Water Valve Sampling During Loop Deadband Wait Time, this value represents the amount of time the water valve relay will be enabled | uint8 | minutes | 0-30 | 74
Holding Register | 40074 | Holding | 73 | FCU Water Valve Sampling During Loop Deadband Wait Time | If FCU water temperature is between FCU Two Pipe Heating Threshold and FCU Two Pipe Cooling Threshold, then if the water valve relay has been enabled for the last FCU Water Valve Sampling During Loop Deadband On Time, this value represents the amount of time the water valve relay will be disabled | uint8 | minutes | 5-255 | 75
Holding Register | 40075 | Holding | 74 | Enable Force Occupied | Configure if Force Occupied feature is enabled/disabled. If Force Occupied = Enable, the Hyperstat will enter occupied mode for duration defined by Forced Occupied Time when occupancy is detected or user interacts with Hyperstat. | bool |  | 0 = Disabled 1 = Enabled | 76
Holding Register | 40076 | Holding | 75 | Enable Auto Away | Configure if Auto Away feature is enabled/disabled. If Auto Away = enabled, the Hyperstat will apply the Auto Away Setback Temps when no motion has been detected for a duration greater than the Auto Away Time | bool |  | 0 = Disabled 1 = Enabled | 77
Holding Register | 40077 | Holding | 76 | Unoccupied Mode | Indicates if occupied or unoccupied settings shall be followed | bool |  | 0 = Occupied 1 = Unoccupied | 78
Holding Register | 40078 | Holding | 77 | Fail Safe Time | Amount of time in minutes after communication is lost before Hyperstat will enter Fail-Safe mode. Modbus Client must poll the Room Temperature Input Register faster than the time defined in this register for communication to be considered valid. | uint16 | minutes | 0-65535 where 0 means fail safe will be disable
Holding Register | 40079 | Holding | 78 | Show Centigrade | Determine if Hyperstat display shall use units of Celcius or Fahrenheit | bool |  | 0 = Disabled 1 = Enabled | 79
Holding Register | 40080 | Holding | 79 | Display CO2 | Configures if CO2 sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 80
Holding Register | 40081 | Holding | 80 | Display PM2.5 | Configures if PM2.5 sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 81
Holding Register | 40082 | Holding | 81 | Display VOC | Configures if VOC sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 82
Holding Register | 40083 | Holding | 82 | Display Humidity | Configures if Humidity sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 83
Holding Register | 40084 | Holding | 83 | System Time Days | Configures the system time of the Hyperstat in days | uint8 |  | 0 = Sunday 1 = Monday 2 = Tuesday 3 = Wednesday 4 = Thursday 5 = Friday 6 = Saturday | 84
Holding Register | 40085 | Holding | 84 | System Time Hours | Configures the system time of the Hyperstat in hours | uint8 | hours | 0-23 | 85
Holding Register | 40086 | Holding | 85 | System Time Minutes | Configures the system time of the Hyperstat in minutes | uint8 | minutes | 0-59 | 86
Holding Register | 40087 | Holding | 86 | DeviceReset | Used to perform a hard reset of the Hyperstat. Note: The Hyperstat will perform a hard reset when this value of "Reset" is written | bool |  | 1 = Reset | 87
Holding Register | 40088 | Holding | 87 | Enable Onboard Temperature & Humidity Sensor | Used to disable the temperature & humidity sensor present within the Hyperstat device. If set to false, Hyperstat will use temperature & humidity read from sensor bus, if present | bool |  | 0 = Onboard T&H sensor disabled 1 = Onboard T&H sensor enabled | 87
Holding Register | 40089 | Holding | 88 | Enable Onboard CO2 & Occupancy Sensor | Used to disable the CO2 & occupancy sensors present within the Hyperstat device. If set to false, Hyperstat will use CO2 & occupancy read from sensor bus, if present | bool |  | 0 = Onboard CO2 & Occupancy sensor disabled 1 = Onboard CO2 & Occupancy sensor enabled | 87
Holding Register | 40090 | Holding | 89 | Cooling Stage 1 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40091 | Holding | 90 | Cooling Stage 2 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40092 | Holding | 91 | Cooling Stage 3 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40093 | Holding | 92 | Heating Stage 1 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40094 | Holding | 93 | Heating Stage 2 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40095 | Holding | 94 | Heating Stage 3 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40096 | Holding | 95 | Linear Fan Speed Low Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40097 | Holding | 96 | Linear Fan Speed Medium Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40098 | Holding | 97 | Linear Fan Speed High Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40099 | Holding | 98 | Staged Fan Speed Low Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40100 | Holding | 99 | Staged Fan Speed Medium Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40101 | Holding | 100 | Staged Fan Speed High Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40102 | Holding | 101 | Staged Fan Default Analog Out Level | Voltage that should be maintained in aout fan stage during dissipation stage when fan turns off | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40103 | Holding | 102 | Minimum Fan Runtime Post Conditioning | Time in minutes before switching the fan completely so that heat/cool is completely dissipated | uint8 | minutes | 0-60
Input Register | 30001 | Input | 0 | Room Temperature | Temperature level sensor reading | uint16 | 1/10 degrees Fahrenheit |  | 88
Input Register | 30002 | Input | 1 | Humidity | Humidity level sensor reading | uint16 | 1/10 % |  | 89
Input Register | 30003 | Input | 2 | CO2 | CO2 level sensor reading | uint16 | ppm |  | 92
Input Register | 30004 | Input | 3 | Occupancy | Occupancy Status | uint8 |  |  | 93
Input Register | 30005 | Input | 4 | Illuminance | Illuminance level sensor reading | uint16 | Lux |  | 91
Input Register | 30006 | Input | 5 | Ultraviolet Index | Ultraviolet Index sensor reading | uint16 |  |  | 90
Input Register | 30007 | Input | 6 | Sound | Sound level sensor reading | uint16 | dB |  | 97
Input Register | 30008 | Input | 7 | VOC | Volatile organic compound sensor reading | uint16 | ppb |  | 94
Input Register | 30009 | Input | 8 | PM2.5 | PM2.5 level sensor reading | uint16 | ug/m3 |  | 95
Input Register | 30010 | Input | 9 | PM10 | PM10 level sensor reading | uint16 | ug/m3 |  | 96
Input Register | 30011 | Input | 10 | Analog Input 1 | Voltage level at analog input 1 | uint16 | 1/10 volts | 0-100 (0.0-10.0) | 98
Input Register | 30012 | Input | 11 | Analog Input 2 | Voltage level at analog input 2 | uint16 | 1/10 volts | 0-100 (0.0-10.0) | 99
Input Register | 30013 | Input | 12 | Thermistor Input 1 | Resistance level reading at thermistor input 1 | uint16 | 1/10 kOhm |  | 100
Input Register | 30014 | Input | 13 | Thermistor Input 2 | Resistance level reading at thermistor input 2 | uint16 | 1/10 kOhm |  | 101
Input Register | 30015 | Input | 14 | Relay 1 | Contains the current value of relay 1 | bool |  | 0 = Off 1 = On | 102
Input Register | 30016 | Input | 15 | Relay 2 | Contains the current value of relay 2 | bool |  | 0 = Off 1 = On | 103
Input Register | 30017 | Input | 16 | Relay 3 | Contains the current value of relay 3 | bool |  | 0 = Off 1 = On | 104
Input Register | 30018 | Input | 17 | Relay 4 | Contains the current value of relay 4 | bool |  | 0 = Off 1 = On | 105
Input Register | 30019 | Input | 18 | Relay 5 | Contains the current value of relay 5 | bool |  | 0 = Off 1 = On | 106
Input Register | 30020 | Input | 19 | Relay 6 | Contains the current value of relay 6 | bool |  | 0 = Off 1 = On | 107
Input Register | 30021 | Input | 20 | Analog Out 1 Percent | PWM channel 1 output level | uint8 | % | 0-100 | 108
Input Register | 30022 | Input | 21 | Analog Out 2 Percent | PWM channel 2 output level | uint8 | % | 0-100 | 109
Input Register | 30023 | Input | 22 | Analog Out 3 Percent | PWM channel 3 output level | uint8 | % | 0-100 | 110
Input Register | 30024 | Input | 23 | Threshold Alert | Bitmap representing each alert thresold (CO2, VOC, PM2.5) | uint16 |  | Bit Index 0 = CO2 Bit Index 1 = VOC Bit Index 2 = PM2.5 | 111
| 30025 | Input | 24 | Operating Mode | Contains the current operating mode of the hyperstat | uint8 | NA | 0 = OFF 1 = HEATING 2 = COOLING
| 30026 | Input | 25 | Active Set Temperature Heating | Active heating temperature setpoint of the Hyperstat | uint16 | 2 x Fahrenheit | 120-180 (60.0 - 90.0)
| 30027 | Input | 26 | Active Set Temperature Cooling | Active ceating temperature setpoint of the Hyperstat | uint16 | 2 x Fahrenheit | 120-180 (60.0 - 90.0)
| 30028 | Input | 27 | Active Conditioning Mode | Active conditioning mode of the hyperstat | uint8 | NA | 0 = OFF 1 = AUTO 2 = HEATING 3 = COOLING
| 30029 | Input | 28 | Active Fan Speed | Active fan speed of hyperstat | uint8 | NA | 0 = OFF 1 = AUTO 2 = LOW 3 = MEDIUM 4 = HIGH
| 30030 | Input | 29 | Occupancy Manager State | Reflects the state of the occupancy manager | uint8 | NA | 0 = INITIALIZING 1 = OCCUPIED 2 = UNOCCUPIED 3 = AUTO AWAY 4 = FORCE OCCUPIED
Input Register | 30031 | Input | 30 | FW Version Major | Major version number component of FW version string | uint8 |  | 0-255 | 132
Input Register | 30032 | Input | 31 | FW Version Minor | Minor version number component of FW version string | uint8 |  | 0-255 | 133
Input Register | 30033 | Input | 32 | Modbus Address | Address of modbus server | uint8 |  | 0-255 | 134
Input Register | 30034 | Input | 33 | Baud Rate | Configured RS485 baud rate | uint8 |  | 0 = 9600 1 = 19200 2 = 38400 3 = 57600 4 = 115200 | 135
Input Register | 30035 | Input | 34 | Parity | Configured RS485 parity bit | uint8 |  | 0 = None 1 = Odd 2 = Even 3 = Mark 4 = Space | 136
Input Register | 30036 | Input | 35 | Stop Bit | Configured RS485 stop bit | uint8 |  | 0 = 1 Stop Bit 1 = 1.5 Stop Bits 2 = 2 Stop Bits | 137
Input Register | 30037 | Input | 36 | Pressure | Different pressure from differential pressure sensor if connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Note on E76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Status or Profile
Note on E120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Discuss with Deep

## Modbus Mapping for Split
Register Type | Register Number | Register Type | Register Address | Parameters | Description | Type | Units | Values | BACnet Object ID
Holding Register | 40001 | Holding | 0 | Set Temperature Heating | Temperature setpoint hyperstat will heat to when operating mode = heating | uint16 | 2 x Fahrenheit | 120-180 (60.0 - 90.0) | 02
Holding Register | 40002 | Holding | 1 | Set Temperature Cooling | Temperature setpoint hyperstat will cool to when operating mode = cooling | uint16 | 2 x Fahrenheit | 120-180 (60.0 - 90.0) | 01
Holding Register | 40003 | Holding | 2 | Fan Speed | Configure the fan speed of hyperstat | uint8 | NA | 0 = OFF 1 = AUTO 2 = LOW 3 = MEDIUM 4 = HIGH | 03
Holding Register | 40004 | Holding | 3 | Conditioning Mode | Configure the conditioning mode of the hyperstat | uint8 | NA | 0 = OFF 1 = AUTO 2 = HEATING 3 = COOLING | 04
Holding Register | 40005 | Holding | 4 | Max Heating User Temp | Maximum heating set temperature user can set | uint16 | degrees Fahrenheit | 60-90 | 06
Holding Register | 40006 | Holding | 5 | Min Heating User Temp | Minimum heating set temperature the user can set | uint16 | degrees Fahrenheit | 60-90 | 07
Holding Register | 40007 | Holding | 6 | Max Cooling User Temp | Maximum cooling set temperature user can set | uint16 | degrees Fahrenheit | 60-90 | 08
Holding Register | 40008 | Holding | 7 | Min Cooling User Temp | Minimum cooling set temperature the user can set | uint16 | degrees Fahrenheit | 60-90 | 09
Holding Register | 40009 | Holding | 8 | Temperature Offset | Offset added to measurement room temperature | int16 | 1/10 degrees Fahrenheit | -100 - 100 (-10.0 - 10.0) | 10
Holding Register | 40010 | Holding | 9 | Heating Deadband | Amount above set temperature at which heating is activated | uint16 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0) | 11
Holding Register | 40011 | Holding | 10 | Cooling Deadband | Amount below set temperature at which cooling is activated | uint16 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0) | 12
Holding Register | 40012 | Holding | 11 | Temperature Mode | Temperature mode defining how temperature setpoints and deadbands can be configured and how they will be applied | uint8 | NA | 0 = Single Setpoint 1 = Dual Setpoint Fixed Deadband 2 = Dual Setpoint Variable Deadband | 13
Holding Register | 40013 | Holding | 12 | Humidity Min Setpoint | Threshold at which hyperstat will attempt to humidify if humidity level is less than | uint8 | % | 20-100 | 14
Holding Register | 40014 | Holding | 13 | Humidity Max Setpoint | Threshold at which hyperstat will attempt to dehumidify if humidity level is greater than | uint8 | % | 20-100 | 15
Holding Register | 40015 | Holding | 14 | CO2 Alert Threshold | Threshold of CO2 level at which an alert will be indicated | uint16 | ppm | 400-10000 | 16
Holding Register | 40016 | Holding | 15 | VOC Alert Threshold | Threshold of VOC level at which an alert will be indicated | uint16 | ppb | 0-10000 | 17
Holding Register | 40017 | Holding | 16 | PM2.5 Alert Threshold | Threshold of PM2.5 level at which an alert will be indicated | uint16 | ug/m3 | 0-10000 | 18
Holding Register | 40018 | Holding | 17 | Profile | Profile in which Hyperstat shall run | uint8 |  | 0 = None (Conv, Split) 1 = Conventional Package Unit (Conv) 2 = Heat Pump Unit (Conv) 3 = 2 Pipe Fancoil Unit (Conv) 4 = 4 Pipe Fancoil Unit (Conv) 5 = Reserved 6 = Sense (Conv) 7 = CPU + ECO (Split) | 19
Holding Register | 40019 | Holding | 18 | Relay 1 Enable | Configure if relay 1 is enabled/disabled Note: Not applicable if Hyperstat Split, Profile = CPU +Economizer | bool |  | 0 = Disabled 1 = Enabled | 20
Holding Register | 40020 | Holding | 19 | Relay 2 Enable | Configure if relay 2 is enabled/disabled Note: Not applicable if Hyperstat Split, Profile = CPU +Economizer | bool |  | 0 = Disabled 1 = Enabled | 21
Holding Register | 40021 | Holding | 20 | Relay 3 Enable | Configure if relay 3 is enabled/disabled Note: Not applicable if Hyperstat Split, Profile = CPU +Economizer | bool |  | 0 = Disabled 1 = Enabled | 22
Holding Register | 40022 | Holding | 21 | Relay 4 Enable | Configure if relay 4 is enabled/disabled Note: Not applicable if Hyperstat Split, Profile = CPU +Economizer | bool |  | 0 = Disabled 1 = Enabled | 23
Holding Register | 40023 | Holding | 22 | Relay 5 Enable | Configure if relay 5 is enabled/disabled Note: Not applicable if Hyperstat Split, Profile = CPU +Economizer | bool |  | 0 = Disabled 1 = Enabled | 24
Holding Register | 40024 | Holding | 23 | Relay 6 Enable | Configure if relay 6 is enabled/disabled Note: Not applicable if Hyperstat Split, Profile = CPU +Economizer | bool |  | 0 = Disabled 1 = Enabled | 25
Holding Register | 40025 | Holding | 24 | Relay 1 Mapping | Configure the mapping of relay 1 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust Fan Stage 1 15 = Exhaust Fan Stage 2 | 26
Holding Register | 40026 | Holding | 25 | Relay 2 Mapping | Configure the mapping of relay 2 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust Fan Stage 1 15 = Exhaust Fan Stage 2 | 27
Holding Register | 40027 | Holding | 26 | Relay 3 Mapping | Configure the mapping of relay 3 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust Fan Stage 1 15 = Exhaust Fan Stage 2 | 28
Holding Register | 40028 | Holding | 27 | Relay 4 Mapping | Configure the mapping of relay 4 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust Fan Stage 1 15 = Exhaust Fan Stage 2 | 29
Holding Register | 40029 | Holding | 28 | Relay 5 Mapping | Configure the mapping of relay 5 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust Fan Stage 1 15 = Exhaust Fan Stage 2 | 30
Holding Register | 40030 | Holding | 29 | Relay 6 Mapping | Configure the mapping of relay 6 Note: This value is only used if the relay is enabled | uint8 |  | 0 = None 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust Fan Stage 1 15 = Exhaust Fan Stage 2 | 31
Holding Register | 40031 | Holding | 30 | Analog In 1 Enable | Configure if analog input 1 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 32
Holding Register | 40032 | Holding | 31 | Analog In 1 Mapping | Configure the mapping of analog input 1 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Current 0-10 1 = Current 0-20 2 = Current 0-50 3 = Keycard 4 = Door Window | 33
Holding Register | 40033 | Holding | 32 | Analog In 2 Enable | Configure if analog input 2 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 34
Holding Register | 40034 | Holding | 33 | Analog In 2 Mapping | Configure the mapping of analog input 2 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Current 0-10 1 = Current 0-20 2 = Current 0-50 3 = Keycard 4 = Door Window | 35
Holding Register | 40035 | Holding | 34 | Analog Out 1 Enable | Configure if analog output 1 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 36
Holding Register | 40036 | Holding | 35 | Analog Out 1 Mapping | Configure the mapping of analog output 1 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Cooling 1 = Fan Speed 2 = Heating 3 = OAO Damper | 37
Holding Register | 40037 | Holding | 36 | Analog Out 1 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 38
Holding Register | 40038 | Holding | 37 | Analog Out 1 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 39
Holding Register | 40039 | Holding | 38 | Analog Out 1 Pulse Enabled | Determines if PWM channel 1 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage | 40
Holding Register | 40040 | Holding | 39 | Analog Out 2 Enable | Configure if analog output 2 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 41
Holding Register | 40041 | Holding | 40 | Analog Out 2 Mapping | Configure the mapping of analog output 2 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Cooling 1 = Fan Speed 2 = Heating 3 = OAO Damper | 42
Holding Register | 40042 | Holding | 41 | Analog Out 2 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 43
Holding Register | 40043 | Holding | 42 | Analog Out 2 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 44
Holding Register | 40044 | Holding | 43 | Analog Out 2 Pulse Enabled | Determines if PWM channel 2 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage | 45
Holding Register | 40045 | Holding | 44 | Analog Out 3 Enable | Configure if analog output 3 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled | 46
Holding Register | 40046 | Holding | 45 | Analog Out 3 Mapping | Configure the mapping of analog output 3 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Cooling 1 = Fan Speed 2 = Heating 3 = OAO Damper | 47
Holding Register | 40047 | Holding | 46 | Analog Out 3 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 48
Holding Register | 40048 | Holding | 47 | Analog Out 3 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0) | 49
Holding Register | 40049 | Holding | 48 | Analog Out 3 Pulse Enabled | Determines if PWM channel 3 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage | 50
Holding Register | 40050 | Holding | 49 | TH1 Airflow Temperature Enable | Enable or disable thermistor input 1 which is used for measuring airflow temperature | bool |  | 0 = Disabled 1 = Enabled | 51
Holding Register | 40051 | Holding | 50 | TH2 Enable | Enable or disable thermistor input 2 which is used for measuring airflow temperature | bool |  | 0 = Disabled 1 = Enabled | 52
Holding Register | 40052 | Holding | 51 | Use TH1 As Room Temp Sensor | When enabled, Hyperstat will use the thermistor connected at TH1 input for determining room/zone temperature instead of the onboard temperature sensor | bool |  | 0 = Disabled 1 = Enabled | 53
Holding Register | 40053 | Holding | 52 | Zone CO2 Damper Opening Rate | TBD | uint8 | %/100 ppm | 0-100 | 54
Holding Register | 40054 | Holding | 53 | Zone CO2 Threshold | Determines the point where Hyperstat starts controlling dampers to maintain CO2 at target value | uint16 | ppm | 0-2000 | 55
Holding Register | 40055 | Holding | 54 | Zone CO2 Target | Target value of CO2 | uint16 | ppm | 0-2000 | 56
Holding Register | 40056 | Holding | 55 | Proportional Constant | Tuner that produces an output action that is proportional to the deviation between the set point and the measured process value for a PI Loop | uint8 | 1/100 | 0-100 | 57
Holding Register | 40057 | Holding | 56 | Integral Constant | Condition with which the controller output is proportional to the amount of time the error is present | uint8 | 1/100 | 0-100 | 58
Holding Register | 40058 | Holding | 57 | Proportional Temperature Range | Defines the band of temperature, or range of temperature, over which the output of the controller is proportional. Example controlling the damper opertions | uint16 | 1/10 degrees Fahrenheit | 0-100 (0.0-10.0) | 59
Holding Register | 40059 | Holding | 58 | Integration Time | Defines the amount of time PI loop in the system integrates the error over a period until error value reaches to zero. It limits the speed of response and affects stability of the system | uint16 | minutes | 5-100 | 60
Holding Register | 40060 | Holding | 59 | Unoccupied Setback | Determines how many degrees from the desired temperature the zone will be allowed to drift during unoccupied | uint8 | 1/10 degrees Fahrenheit | 10-200 (1.0-20.0) | 61
Holding Register | 40061 | Holding | 60 | Relay Activation Hysteresis | Condition at which relay will turn off after being turned on to control based on load | uint8 | % | 1-50 | 62
Holding Register | 40062 | Holding | 61 | Analog Fan Speed Multiplier | Tuner that determines how fast a fan can move based on heating or cooling load | uint8 | 1/10 | 1-100 (0.1-10) | 63
Holding Register | 40063 | Holding | 62 | Humidity Hysteresis | Tuner that determines a condition at which humidier / dehumidifier will turn off after being turned on to control inside humidity | uint8 | % | 1-100 | 64
Holding Register | 40064 | Holding | 63 | Forced Occupied Time | During unoccupied time in case there is occupancy detected or user interacts with or edits user intent points then system enters in occupied mode for this tuner period only | uint8 | minutes | 0-255 | 65
Holding Register | 40065 | Holding | 64 | Auto Away Time | During Occupied period of the zone (Not during preconditioning period), If an Occupant is not detected for this tuner duration, the zone should enter 'Auto Away' mode if occupancy is enabled | uint8 | minutes | 0-255 | 66
Holding Register | 40066 | Holding | 65 | Auto Away Zone Setback Temp | Determines how many degrees from the desired temperature the zone will be allowed to drift during auto away | uint8 | 1/10 Degrees Fahrenheit | 10-200 (1.0 - 20.0) | 67
Holding Register | 40067 | Holding | 66 | FCU Aux Heating 1 Activate | Represents the difference between the current temp and heating desired temp in which the FCU Aux Heating 1 will activate. For example, if any relay is enabled and associated with Aux Heating State 1, the relay will be activated when currentTemp < Heating Desired Temp - FCU Aux Heating 1 Activate | uint8 | 1/10 Degrees Fahrenheit | 10-100 (1.0 - 10.0) | 68
Holding Register | 40068 | Holding | 67 | FCU Aux Heating 2 Activate | Represents the difference between the current temp and heating desired temp in which the FCU Aux Heating 2 will activate. For example, if any relay is enabled and associated with Aux Heating State 2, the relay will be activated when currentTemp < Heating Desired Temp - FCU Aux Heating 2 Activate | uint8 | 1/10 Degrees Fahrenheit | 10-100 (1.0 - 10.0) | 69
Holding Register | 40069 | Holding | 68 | FCU Two Pipe Heating Threshold | For a 2 pipe FCU, this tuner determines if the central plant is providing hot water when compared to supply water temp sensor. If Th2 (Supply water sensor) is more than 2pipeFancoilHeatingThreshold (85) then the central plant is providing hot water | uint8 | Degrees Fahrenheit | 70-130 | 70
Holding Register | 40070 | Holding | 69 | FCU Two Pipe Cooling Threshold | For a 2 pipe FCU, this tuner determines if the central plant is providing cold water when compared to supply water temp sensor. If Th2 (supply water sensor) is less than 2pipeFancoilCoolingThreshold (65) then the central plant is providing cold water | uint8 | Degrees Fahrenheit | 35-70 | 71
Holding Register | 40071 | Holding | 70 | FCU Water Valve Sampling On Time | If FCU water temperature is greater than FCU Two Pipe Heating Threshold Amount or less than FCU Two Pipe Cooling Threshold, then if the water valve relay has not been enabled for the last FCU Water Valve Sampling Wait Time, this value represents the amount of time the water valve relay will be enabled | uint8 | minutes | 0-30 | 72
Holding Register | 40072 | Holding | 71 | FCU Water Valve Sampling Wait Time | If FCU water temperature is greater than FCU Two Pipe Heating Threshold Amount or less than FCU Two Pipe Cooling Threshold, then if the water valve relay has been enabled for the last FCU Water Valve Sampling On Time, this value represents the amount of time the water valve relay will be disabled | uint8 | minutes | 5-255 | 73
Holding Register | 40073 | Holding | 72 | FCU Water Valve Sampling During Loop Deadband On Time | If FCU water temperature is between FCU Two Pipe Heating Threshold and FCU Two Pipe Cooling Threshold, then if the water valve relay has not been enabled for the last FCU Water Valve Sampling During Loop Deadband Wait Time, this value represents the amount of time the water valve relay will be enabled | uint8 | minutes | 0-30 | 74
Holding Register | 40074 | Holding | 73 | FCU Water Valve Sampling During Loop Deadband Wait Time | If FCU water temperature is between FCU Two Pipe Heating Threshold and FCU Two Pipe Cooling Threshold, then if the water valve relay has been enabled for the last FCU Water Valve Sampling During Loop Deadband On Time, this value represents the amount of time the water valve relay will be disabled | uint8 | minutes | 5-255 | 75
Holding Register | 40075 | Holding | 74 | Enable Force Occupied | Configure if Force Occupied feature is enabled/disabled. If Force Occupied = Enable, the Hyperstat will enter occupied mode for duration defined by Forced Occupied Time when occupancy is detected or user interacts with Hyperstat. | bool |  | 0 = Disabled 1 = Enabled | 76
Holding Register | 40076 | Holding | 75 | Enable Auto Away | Configure if Auto Away feature is enabled/disabled. If Auto Away = enabled, the Hyperstat will apply the Auto Away Setback Temps when no motion has been detected for a duration greater than the Auto Away Time | bool |  | 0 = Disabled 1 = Enabled | 77
Holding Register | 40077 | Holding | 76 | Unoccupied Mode | Indicates if occupied or unoccupied settings shall be followed | bool |  | 0 = Occupied 1 = Unoccupied | 78
Holding Register | 40078 | Holding | 77 | Fail-Safe Time | Determines the amount of time in minutes in which | uint16 | minutes | 0-65535 where 0 means fail safe will be disable
Holding Register | 40079 | Holding | 78 | Show Centigrade | Determine if Hyperstat display shall use units of Celcius or Fahrenheit | bool |  | 0 = Disabled 1 = Enabled | 79
Holding Register | 40080 | Holding | 79 | Display CO2 | Configures if CO2 sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 80
Holding Register | 40081 | Holding | 80 | Display PM2.5 | Configures if PM2.5 sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 81
Holding Register | 40082 | Holding | 81 | Display VOC | Configures if VOC sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 82
Holding Register | 40083 | Holding | 82 | Display Humidity | Configures if Humidity sensor value is displayed on Hyperstat home screen | bool |  | 0 = Disabled 1 = Enabled | 83
Holding Register | 40084 | Holding | 83 | System Time Days | Configures the system time of the Hyperstat in days | uint8 |  | 0 = Sunday 1 = Monday 2 = Tuesday 3 = Wednesday 4 = Thursday 5 = Friday 6 = Saturday | 84
Holding Register | 40085 | Holding | 84 | System Time Hours | Configures the system time of the Hyperstat in hours | uint8 | hours | 0-23 | 85
Holding Register | 40086 | Holding | 85 | System Time Minutes | Configures the system time of the Hyperstat in minutes | uint8 | minutes | 0-59 | 86
Holding Register | 40087 | Holding | 86 | DeviceReset | Used to perform a hard reset of the Hyperstat. Note: The Hyperstat will perform a hard reset when this value of "Reset" is written | bool |  | 1 = Reset | 87
Holding Register | 40088 | Holding | 87 | Enable Onboard Temperature & Humidity Sensor | Used to disable the temperature & humidity sensor present within the Hyperstat device. If set to false, Hyperstat will use temperature & humidity read from sensor bus, if present | bool |  | 0 = Onboard T&H sensor disabled 1 = Onboard T&H sensor enabled | 87
Holding Register | 40089 | Holding | 88 | Enable Onboard CO2 & Occupancy Sensor | Used to disable the CO2 & occupancy sensors present within the Hyperstat device. If set to false, Hyperstat will use CO2 & occupancy read from sensor bus, if present | bool |  | 0 = Onboard CO2 & Occupancy sensor disabled 1 = Onboard CO2 & Occupancy sensor enabled | 87
Holding Register | 40090 | Holding | 89 | Cooling Stage 1 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40091 | Holding | 90 | Cooling Stage 2 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40092 | Holding | 91 | Cooling Stage 3 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40093 | Holding | 92 | Heating Stage 1 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40094 | Holding | 93 | Heating Stage 2 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40095 | Holding | 94 | Heating Stage 3 Fan Output | Voltage at which the cooler/damper/fan is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40096 | Holding | 95 | Linear Fan Speed Low Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40097 | Holding | 96 | Linear Fan Speed Medium Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40098 | Holding | 97 | Linear Fan Speed High Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40099 | Holding | 98 | Staged Fan Speed Low Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40100 | Holding | 99 | Staged Fan Speed Medium Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40101 | Holding | 100 | Staged Fan Speed High Level | Percentage | uint8 | % | 0 - 100
Holding Register | 40102 | Holding | 101 | Staged Fan Default Analog Out Level | Voltage that should be maintained in aout fan stage during dissipation stage when fan turns off | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40103 | Holding | 102 | Minimum Fan Runtime Post Conditioning | Time in minutes before switching the fan completely so that heat/cool is completely dissipated | uint8 | minutes | 0-60
Holding Register | 40104 | Holding | 103 | Relay 7 Enable | Configure if relay 7 is enabled/disabled Note: The value in this register shall be ignored for Hyperstat Split, Profile = CPU + Economizer. The mapping register contains a "Disabled" state | bool |  | 0 = Disabled 1 = Enabled
Holding Register | 40105 | Holding | 104 | Relay 8 Enable | Configure if relay 8 is enabled/disabled Note: The value in this register shall be ignored for Hyperstat Split, Profile = CPU + Economizer. The mapping register contains a "Disabled" state | bool |  | 0 = Disabled 1 = Enabled
Holding Register | 40106 | Holding | 105 | Relay 7 Mapping | Configure the mapping of relay 7 Note: This value is only used if the relay is enabled | uint8 |  | 0 = Disabled 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust 1 15 = Exhaust 2
Holding Register | 40107 | Holding | 106 | Relay 8 Mapping | Configure the mapping of relay 8 Note: This value is only used if the relay is enabled | uint8 |  | 0 = Disabled 1 = Cooling Stage 1 2 = Cooling Stage 2 3 = Cooling Stage 3 4 = Heating Stage 1 5 = Heating Stage 2 6 = Heating Stage 3 7 = Fan Low Speed 8 = Fan Medium Speed 9 = Fan High Speed 10 = Fan Enable 11 = Occupied Enable 12 = Humidifier 13 = Dehumidifier 14 = Exhaust 1 15 = Exhaust 2
Holding Register | 40108 | Holding | 107 | Analog Out 4 Enable | Configure if analog output 4 is enabled/disabled | bool |  | 0 = Disabled 1 = Enabled
Holding Register | 40109 | Holding | 108 | Analog Out 4 Mapping | Configure the mapping of analog output 4 Note: This value is only used if the analog input is enabled | uint8 |  | 0 = Disabled 1 = Cooling 2 = Linear Fan 3 = Heating 4 = OAO Dampler 5 = Staged Fan
Holding Register | 40110 | Holding | 109 | Analog Out 4 At Min Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at minimum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40111 | Holding | 110 | Analog Out 4 At Max Setting | Voltage at which the cooler/damper/fan mapped to the analog output is at maximum position | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Holding Register | 40112 | Holding | 111 | Analog Out 4 Pulse Enabled | Determines if PWM channel 4 shall be a pulsed or constant voltage | bool |  | 0 = Constant Voltage 1 = Pulsed Voltage
Holding Register | 40113 | Holding | 112 | Universal Input Mapping 1 | Configure the mapping of Universal Input 1 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40114 | Holding | 113 | Universal Input Mapping 2 | Configure the mapping of Universal Input 2 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40115 | Holding | 114 | Universal Input Mapping 3 | Configure the mapping of Universal Input 3 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40116 | Holding | 115 | Universal Input Mapping 4 | Configure the mapping of Universal Input 4 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40117 | Holding | 116 | Universal Input Mapping 5 | Configure the mapping of Universal Input 5 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40118 | Holding | 117 | Universal Input Mapping 6 | Configure the mapping of Universal Input 6 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40119 | Holding | 118 | Universal Input Mapping 7 | Configure the mapping of Universal Input 7 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40120 | Holding | 119 | Universal Input Mapping 8 | Configure the mapping of Universal Input 8 | uint8 |  | 0 = Disabled 1 = Generic Voltage 2 = Generic Resistance 3 = Current 0-10 4 = Current 0-20 5 = Current 0-50 6 = Current 0-100 7 = Current 0-150 8 = SAT 9 = MAT 10 = OAT 11 = Filter NO 12 = Filter NC 13 = Condensate NO 14 = Condensate NC 15 = Pressure 0-1 16 = Pressure 0-2
Holding Register | 40121 | Holding | 120 | Sensor Bus Mapping Address 0 | Configure the mapping of Connect-Module sensor bus address 0 | uint8 |  | 0 = Disabled 1 = SAT 2 = MAT 3 = OAT 4 = Pressure
Holding Register | 40122 | Holding | 121 | Sensor Bus Mapping Address 1 | Configure the mapping of Connect-Module sensor bus address 1 | uint8 |  | 0 = Disabled 1 = SAT 2 = MAT 3 = OAT 4 = Pressure
Holding Register | 40123 | Holding | 122 | Sensor Bus Mapping Address 2 | Configure the mapping of Connect-Module sensor bus address 2 | uint8 |  | 0 = Disabled 1 = SAT 2 = MAT 3 = OAT 4 = Pressure
Holding Register | 40124 | Holding | 123 | Sensor Bus Mapping Address 3 | Configure the mapping of Connect-Module sensor bus address 3 | uint8 |  | 0 = Disabled 1 = SAT 2 = MAT 3 = OAT 4 = Pressure
Holding Register | 40125 | Holding | 124 | Economizing to Main Cooling Loop Map | First percentage of cooling loop out that analog modulating output needs to be mapped to | uint16 |  | 0-100
Holding Register | 40126 | Holding | 125 | Economizing Temperature Minimum | When the outside temperature is below this temperature economizer function will not work. DCV will still be active and CO2 levels will determine the OAO damper opening | uint16 | Degrees Fahrenheit | 0-80
Holding Register | 40127 | Holding | 126 | Economizing Temperature Maximum | When the outside temperature is above this value the economizer function will not work and OAO will close to its minimum position or the position determined by the CO2 level. | uint16 | Degrees Fahrenheit | 0-120
Holding Register | 40128 | Holding | 127 | Economizing Humidity Minimum | Minimum humidity level that the outside air must be before the system will open the OAO for enthalpy economizing. | uint16 | % | 0-100
Holding Register | 40129 | Holding | 128 | Economizing Humidity Maximum | Maximum humidity level allowed for enthalpy economizing. If the outside humidity is above this level the OAO will close to the minimum value set by DCV. | uint16 | % | 0-100
Holding Register | 40130 | Holding | 129 | Economizing Dry Bulb Threshold |  | uint16 | Degrees Fahrenheit | 0-70
Holding Register | 40115 | Holding | 114 | Enthalpy Duct Compensation Offset | This is a compensation factor that is added to the OAE (outside air enthalpy ) for the comparison with IAE (indoor air average enthalpy). Economizer function is available if: OAE + DCO < IAE, economizing = true | uint16 | BTU/lb | 0-10
Holding Register | 40116 | Holding | 115 | Duct Compensation Offset |  | uint16 | Degrees Fahrenheit | 0-10
Holding Register | 40117 | Holding | 116 | Exhaust Fan Threshold Stage 1 |  | uint16 | % | 0-100
Holding Register | 40118 | Holding | 117 | Exhaust Fan Threshold Stage 2 |  | uint16 | % | 0-100
Holding Register | 40119 | Holding | 118 | Exhaust Fan Hysteresis |  | uint16 | % | 0-50
Holding Register | 40120 | Holding | 119 | Outside Damper MAT Target |  | uint16 | Degrees Fahrenheit | 30-60
Holding Register | 40131 | Holding | 130 | Enthalpy Duct Compensation Offset | This is a compensation factor that is added to the OAE (outside air enthalpy ) for the comparison with IAE (indoor air average enthalpy). Economizer function is available if: OAE + DCO < IAE, economizing = true | uint16 | BTU/lb | 0-10
Holding Register | 40132 | Holding | 131 | Duct Compensation Offset
Holding Register | 40133 | Holding | 132 | Exhaust Fan Stage 1 Threshold
Holding Register | 40134 | Holding | 133 | Exhaust Fan Stage 2 Threshold
Holding Register | 40135 | Holding | 134 | Exhaust Fan Hysteresis
| 40136 |  | 135 | Outside Damper Mixed Air Target
Holding Register | 40137 | Holding | 136 | Outside Damper Mixed Air Minimum |  | uint16 | Degrees Fahrenheit | 0-100
Holding Register | 40138 | Holding | 137 | Outside Damper Minimum Open | To set a minimum open position of the economizer actuator. If to meet code you need to have a minimum open position of 20%, then you would set this value to 20. | uint16 | % | 0-100
Holding Register | 40139 | Holding | 138 | Staged Fan Default Analog Out Level | Voltage that should be maintained in aout fan stage during dissipation stage when fan turns off | uint8 | 1/10 Volts | 0 - 100 (0.0 - 10.0)
Input Register | 30001 | Input | 0 | Room Temperature | Temperature level sensor reading | uint16 | 1/10 degrees Fahrenheit |  | 88
Input Register | 30002 | Input | 1 | Humidity | Humidity level sensor reading | uint16 | 1/10 % |  | 89
Input Register | 30003 | Input | 2 | CO2 | CO2 level sensor reading | uint16 | ppm |  | 92
Input Register | 30004 | Input | 3 | Occupancy | Occupancy Status | uint8 |  |  | 93
Input Register | 30005 | Input | 4 | Illuminance | Illuminance level sensor reading | uint16 | Lux |  | 91
Input Register | 30006 | Input | 5 | Ultraviolet Index | Ultraviolet Index sensor reading | uint16 |  |  | 90
Input Register | 30007 | Input | 6 | Sound | Sound level sensor reading | uint16 | dB |  | 97
Input Register | 30008 | Input | 7 | VOC | Volatile organic compound sensor reading | uint16 | ppb |  | 94
Input Register | 30009 | Input | 8 | PM2.5 | PM2.5 level sensor reading | uint16 | ug/m3 |  | 95
Input Register | 30010 | Input | 9 | PM10 | PM10 level sensor reading | uint16 | ug/m3 |  | 96
Input Register | 30011 | Input | 10 | Analog Input 1 | Voltage level at analog input 1 | uint16 | 1/10 volts | 0-100 (0.0-10.0) | 98
Input Register | 30012 | Input | 11 | Analog Input 2 | Voltage level at analog input 2 | uint16 | 1/10 volts | 0-100 (0.0-10.0) | 99
Input Register | 30013 | Input | 12 | Thermistor Input 1 | Resistance level reading at thermistor input 1 | uint16 | 1/10 kOhm |  | 100
Input Register | 30014 | Input | 13 | Thermistor Input 2 | Resistance level reading at thermistor input 2 | uint16 | 1/10 kOhm |  | 101
Input Register | 30015 | Input | 14 | Relay 1 | Contains the current value of relay 1 | bool |  | 0 = Off 1 = On | 102
Input Register | 30016 | Input | 15 | Relay 2 | Contains the current value of relay 2 | bool |  | 0 = Off 1 = On | 103
Input Register | 30017 | Input | 16 | Relay 3 | Contains the current value of relay 3 | bool |  | 0 = Off 1 = On | 104
Input Register | 30018 | Input | 17 | Relay 4 | Contains the current value of relay 4 | bool |  | 0 = Off 1 = On | 105
Input Register | 30019 | Input | 18 | Relay 5 | Contains the current value of relay 5 | bool |  | 0 = Off 1 = On | 106
Input Register | 30020 | Input | 19 | Relay 6 | Contains the current value of relay 6 | bool |  | 0 = Off 1 = On | 107
Input Register | 30021 | Input | 20 | Analog Out 1 Percent | PWM channel 1 output level | uint8 | % | 0-100 | 108
Input Register | 30022 | Input | 21 | Analog Out 2 Percent | PWM channel 2 output level | uint8 | % | 0-100 | 109
Input Register | 30023 | Input | 22 | Analog Out 3 Percent | PWM channel 3 output level | uint8 | % | 0-100 | 110
Input Register | 30024 | Input | 23 | Threshold Alert | Bitmap representing each alert thresold (CO2, VOC, PM2.5) | uint16 |  | Bit Index 0 = CO2 Bit Index 1 = VOC Bit Index 2 = PM2.5 | 111
Input Register | 30031 | Input | 30 | FW Version Major | Major version number component of FW version string | uint8 |  | 0-255 | 132
Input Register | 30032 | Input | 31 | FW Version Minor | Minor version number component of FW version string | uint8 |  | 0-255 | 133
Input Register | 30033 | Input | 32 | Modbus Address | Address of modbus server | uint8 |  | 0-255 | 134
Input Register | 30034 | Input | 33 | Baud Rate | Configured RS485 baud rate | uint8 |  | 0 = 9600 1 = 19200 2 = 38400 3 = 57600 4 = 115200 | 135
Input Register | 30035 | Input | 34 | Parity | Configured RS485 parity bit | uint8 |  | 0 = None 1 = Odd 2 = Even 3 = Mark 4 = Space | 136
Input Register | 30036 | Input | 35 | Stop Bit | Configured RS485 stop bit | uint8 |  | 0 = 1 Stop Bit 1 = 1.5 Stop Bits 2 = 2 Stop Bits | 137
Input Register | 30037 | Input | 36 | Pressure | Different pressure from differential pressure sensor if connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Input Register | 30038 | Input | 37 | Relay 7 | Contains the current value of relay 7 | bool |  | 0 = Off 1 = On
Input Register | 30039 | Input | 38 | Relay 8 | Contains the current value of relay 8 | bool |  | 0 = Off 1 = On
Input Register | 30034 | Input | 39 | Analog Out 4 Percent | PWM channel 4 output level | uint8 | % | 0-100
Input Register | 30041 | Input | 40 | Universal Input Mode 1 | Mode of Universal Input 1 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30042 | Input | 41 | Universal Input Value 1 | Value of Universal Input 1 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30043 | Input | 42 | Universal Input Mode 2 | Mode of Universal Input 2 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30044 | Input | 43 | Universal Input Value 2 | Value of Universal Input 2 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30045 | Input | 44 | Universal Input Mode 3 | Mode of Universal Input 3 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30046 | Input | 45 | Universal Input Value 3 | Value of Universal Input 3 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30047 | Input | 46 | Universal Input Mode 4 | Mode of Universal Input 4 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30048 | Input | 47 | Universal Input Value 4 | Value of Universal Input 4 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30049 | Input | 48 | Universal Input Mode 5 | Mode of Universal Input 5 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30050 | Input | 49 | Universal Input Value 5 | Value of Universal Input 5 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30051 | Input | 50 | Universal Input Mode 6 | Mode of Universal Input 6 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30052 | Input | 51 | Universal Input Value 6 | Value of Universal Input 6 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30053 | Input | 52 | Universal Input Mode 7 | Mode of Universal Input 7 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30054 | Input | 53 | Universal Input Value 7 | Value of Universal Input 7 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30055 | Input | 54 | Universal Input Mode 8 | Mode of Universal Input 8 | uint16 |  | 0 = Voltage 1 = Thermistor
Input Register | 30056 | Input | 55 | Universal Input Value 8 | Value of Universal Input 8 If Mode = Voltage, Value represented as millivolts If Mode = Thermistor, Value represented as ohms | uint16 | If Mode = Voltage, Units = Millivolts If Mode = Thermistor, Units = Ohms*10 | 0-10000 (0.0 - 10.0V) 0 - 65000 (0 - 650kOhm)
Input Register | 30057 | Input | 56 | Connect-Module Sensor Bus Temperature Average | Average temperature value of all connected sensors on Connect-Module's one-wire sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 degrees Fahrenheit
Input Register | 30058 | Input | 57 | Connect-Module Sensor Bus Address 0 Temperature | Temperature value of OWI sensor address 0 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 degrees Fahrenheit
Input Register | 30059 | Input | 58 | Connect-Module Sensor Bus Address 1 Temperature | Temperature value of OWI sensor address 1 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 degrees Fahrenheit
Input Register | 30060 | Input | 59 | Connect-Module Sensor Bus Address 2 Temperature | Temperature value of OWI sensor address 2 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 degrees Fahrenheit
Input Register | 30061 | Input | 60 | Connect-Module Sensor Bus Address 3 Temperature | Temperature value of OWI sensor address 3 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 degrees Fahrenheit
Input Register | 30062 | Input | 61 | Connect-Module Sensor Bus Humidity Average | Average humidity value of all connected sensors on Connect-Module's one-wire sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 % | 0-1000 (0-100%)
Input Register | 30063 | Input | 62 | Connect-Module Sensor Bus Address 0 Humidity | Humidity value of OWI sensor address 0 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 % | 0-1000 (0-100%)
Input Register | 30064 | Input | 63 | Connect-Module Sensor Bus Address 1 Humidity | Humidity value of OWI sensor address 1 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 % | 0-1000 (0-100%)
Input Register | 30065 | Input | 64 | Connect-Module Sensor Bus Address 2 Humidity | Humidity value of OWI sensor address 2 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 % | 0-1000 (0-100%)
Input Register | 30066 | Input | 65 | Connect-Module Sensor Bus Address 3 Humidity | Humidity value of OWI sensor address 3 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | 1/10 % | 0-1000 (0-100%)
Input Register | 30067 | Input | 66 | Connect-Module Sensor Bus CO2 Average | Average CO2 value of all connected sensors on Connect-Module's one-wire sensor bus interface Note: Should be 0 if not connected | uint16 | PPM
Input Register | 30068 | Input | 67 | Connect-Module Sensor Bus Address 0 CO2 | CO2 value of OWI sensor address 0 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | PPM
Input Register | 30069 | Input | 68 | Connect-Module Sensor Bus Address 1 CO2 | CO2 value of OWI sensor address 1 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | PPM
Input Register | 30070 | Input | 69 | Connect-Module Sensor Bus Address 2 CO2 | CO2 value of OWI sensor address 2 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | PPM
Input Register | 30071 | Input | 70 | Connect-Module Sensor Bus Address 3 CO2 | CO2 value of OWI sensor address 3 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 | PPM
Input Register | 30072 | Input | 71 | Connect-Module Sensor Bus Pressure Average | Average Pressure value of all connected sensors on Connect-Module's one-wire sensor bus interface Note: Should be 0 if not connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Input Register | 30073 | Input | 72 | Connect-Module Sensor Bus Address 0 Pressure | Pressure value of OWI sensor address 0 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Input Register | 30074 | Input | 73 | Connect-Module Sensor Bus Address 1 Pressure | Pressure value of OWI sensor address 1 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Input Register | 30075 | Input | 74 | Connect-Module Sensor Bus Address 2 Pressure | Pressure value of OWI sensor address 2 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Input Register | 30076 | Input | 75 | Connect-Module Sensor Bus Address 3 Pressure | Pressure value of OWI sensor address 3 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | 12 bit 1's complement, where bit[11] indicates if value is positive or negative | PSI | -500 - 500
Input Register | 30077 | Input | 76 | Connect-Module Sensor Bus Occupancy Average | Average Occupancy value of all connected sensors on Connect-Module's one-wire sensor bus interface Note: Should be 0 if not connected | uint16 |  | 0 = Occupant Not Detected 1 = Occupant Detected
Input Register | 30078 | Input | 77 | Connect-Module Sensor Bus Address 0 Occupancy | Occupancy value of OWI sensor address 0 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 |  | 0 = Occupant Not Detected 1 = Occupant Detected
Input Register | 30079 | Input | 78 | Connect-Module Sensor Bus Address 1 Occupancy | Occupancy value of OWI sensor address 1 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 |  | 0 = Occupant Not Detected 1 = Occupant Detected
Input Register | 30080 | Input | 79 | Connect-Module Sensor Bus Address 2 Occupancy | Occupancy value of OWI sensor address 2 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 |  | 0 = Occupant Not Detected 1 = Occupant Detected
Input Register | 30081 | Input | 80 | Connect-Module Sensor Bus Address 3 Occupancy | Occupancy value of OWI sensor address 3 on Connect-Module's sensor bus interface Note: Should be 0 if not connected | uint16 |  | 0 = Occupant Not Detected 1 = Occupant Detected
Note on E76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Status or Profile
Note on E122: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Discuss with Deep
Note on E162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Discuss with Deep